## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Executive Engineer Cum Project Manager Jal Shakti Vibhag, Division Nalagarh, Himachal Pradesh
Name of Work: Providing Irrigation Facility under HP SHIVA Project for Kunihar and Nalagarh Block, District Solan (Himachal Pradesh) – Package - 1
Contract No: HPSHIVA/OCB-CWJ/IRG/SLN-01/2022-23
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT including Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Civil Work | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2 | RCC Check Dam : Designing, Constructing, Testing & Commissioning ( to be approved by the competent authority) and Construction of RCC Check Dam as per drawings complete in all respects to the entire satisfaction of the Engineer-in-charge. The contractor shall provide 6 sets of approved drawing and design with one soft copy to the department.for the following size- | BI01010001010000000000000515BI0100001113 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | 15 meter length and 2.0 meter depth, At LIS Ser-Delag, LIS Datti and LIS Giana | BI01010001010000000000000515BI0100001114 | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | 20 meter length and 2.0 meter depth, At LIS Sai, LIS Daseran, LIS Pajeena and LIS Chunad | BI01010001010000000000000515BI0100001115 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | RCC Intake Structure at LIS Jailang:- Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) of RCC intake Structure as per drawings, having RCC structure, Roofing with RCC slab, allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling ,MCB DBs,receptacle system & accessories etc., Walk way/ passage CI Rungs inside the structure from top to bottom and steel stair case from ground level to top of intake with connecting path having suitable capacity crane/ hoist arrangement for handling of pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge. Refer Data Sheet No-1 | BI01010001010000000000000515BI0100001116 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4 | RCC Intake Structure at LIS Doli::- Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) of RCC intake Structure as per drawings, having RCC structure, Roofing with RCC slab, allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling ,MCB DBs,receptacle system & accessories etc., Walk way/ passage CI Rungs inside the structure from top to bottom and steel stair case from ground level to top of intake with connecting path having suitable capacity crane/ hoist arrangement for handling of pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge. for . Refer Data Sheet No-1 | BI01010001010000000000000515BI0100001117 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5 | Tube Well at LIS Palli and Beli Khol 1 :- Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) of Tube Well as per drawings including allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling, MCB DBs & switchboards, receptacle system & accessories etc., mono rail with chain pulley arrangement of suitable capacity for lowering/ lifting the pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge. | BI01010001010000000000000515BI0100001118 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | Percolation well:- Designing, Constructing, Testing & Commissioning ( to be approved by the competent authority) and Construction of Percolation well with 3.00 mtr internal diameter and 9.00 mtr depth ,having RCC Circular structure, Roofing with RCC slab, allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling, MCB DBs, receptacles system & accessories etc., Walk way/passage CI Rungs inside the percolation from top to bottom and steel stair case from ground level to top of percolation well with connecting path having suitable capacity crane/ hoist arrangement for handling of pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge. Refer Data Sheet No-2 | BI01010001010000000000000515BI0100001119 | 4 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | Improvement of Kuchha Drain including survey, Soil investigation, cutting - Filling including excavation in all types of strata and foundation concrete, all labour and material charges,complete as per entire satisfaction of engineer-charge.At LIS Ser-Delag | BI01010001010000000000000515BI0100001120 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8 | PUMP HOUSE:- Designing, Constructing, Testing & Commissioning of Pump House & Chowkidar Room at following locations including all allied Civil Works, Electrical Works including lighting fixtures, fans, street / area lighting using poles, associated cabling/ wiring, MCB DBs, receptacle system & accessories etc., Sanitary Work, Site Development, Cutting/ Excavation in all kinds of soils, c/o PCC/ RCC Retaining walls, Breast walls, Toilets, Septic Tanks, External Solar powered Street lighting, External landscaping, Fire Fighting arrangement, Building Lightning Protection System (where applicable), Gantry Crane, dewatering etc complete as directed by engineer in charge The rates quoted by the contractor shall be for the complete work. All ancillary works and accessories required to make the system fully functional shall be included in the cost of work. Nothing extra shall be paid on this account. Refer Data Sheet No-3 | BI01010001010000000000000515BI0100001121 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
8.01 | Pump house of 35.00 Sqm. Area -Kunihar Block | BI01010001010000000000000515BI0100001122 | 6 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
8.02 | Pump house of 35.00 Sqm. Area - Nalagarh Block | BI01010001010000000000000515BI0100001123 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.03 | Pump house of 70.00 Sqm. Area | BI01010001010000000000000515BI0100001124 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9 | Designing, Constructing, Testing & Commissioning of Desilting tank including civil work, Necessary valves & fittings, tube settler media etc. complete in all respect as per the drawings & technical specification.for the followings size- Refer Data Sheet No-4 | BI01010001010000000000000515BI0100001125 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
9.01 | 48 KL Capacity at LIS Ser-Delag, LIS Chunad and LIS Doli | BI01010001010000000000000515BI0100001126 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.02 | 36 KL Capacity at LIS Sai, LIS Datti, LIS Giana and LIS Pajeena | BI01010001010000000000000515BI0100001127 | 4 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.03 | 27 KL Capacity at LIS Jailang | BI01010001010000000000000515BI0100001128 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.04 | 64 KL Capacity at LIS Daseran | BI01010001010000000000000515BI0100001129 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.05 | 140 KL Capacity at LIS Batiakh | BI01010001010000000000000515BI0100001130 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.06 | 320 KL Capacity at LIS Sour | BI01010001010000000000000515BI0100001131 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10 | Designing, Constructing, Testing & Commissioning of Sump well including civil work, Necessary valves & fittings etc. complete in all respect as per the drawings & technical specification.for the followings size- | BI01010001010000000000000515BI0100001132 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
10.01 | 18 KL Capacity at LIS Jailang, LIS Datti, LIS Giana and LIS Pajeena | BI01010001010000000000000515BI0100001133 | 4 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.02 | 18 KL Capacity at LIS Palli and LIS Beli Khol-1 | BI01010001010000000000000515BI0100001134 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.03 | 36 KL Capacity at LIS Daseran | BI01010001010000000000000515BI0100001135 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.04 | 24 KL Capacity at LIS Chunad and LIS Doli | BI01010001010000000000000515BI0100001136 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.05 | 64 KL Capacity at LIS Batiakh | BI01010001010000000000000515BI0100001137 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.06 | 168 KL Capacity at LIS Sour | BI01010001010000000000000515BI0100001138 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
11 | Excavation in foundation, trenches (for pipes & pits) upto all depths in all classification of earth work such as pick work, jumper work, saturated soil including bailing and pumping out water, blasting soft/ hard rock or chieselling soft/hard rock where blasting is prohibited in all lifts including trimming and dressing of sides, leveling of beds to correct grade i/c shoring /strutting , planking, timbering & dewatering wherever required, stacking the useable & unuseable material /soil separately & after laying jointing & testing of pipes, returning the useable soil in trenches in 15 cm layers including consolidating of such deposoited layer by ramming & watering & then disposing of all surplus excavated soil /unusable material as directed with in all leads & lifts Excluding restoration metalled surfaces to its original condition( Will be paid Separately) & including cost of diversion for traffic, night signals, fixing caution boards, crossing over trenches for access to houses, fencing etc. complete in all respects with in all leads & lifts as per directions of Engineer-in-charge. | BI01010001010000000000000515BI0100001139 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
11.01 | Kunihar Block | BI01010001010000000000000515BI0100001140 | 7637.4 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11.02 | Nalagarh Block | BI01010001010000000000000515BI0100001141 | 12100.12 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12 | Providing ,Laying,jointing & testing of Galvanised Mild steel tube with flange / Butt welding of approved make or by JSV Deptt (list attached) conforming to BIS 1239-2004 ( with upto date ammendements ) of following diameter and class including all specials and fittings as required complete as per actual site condition with in all leads and lifts as per the direction and to the entire satisfaction of Engineer-in Charge. The pipe shall be factory galvanized as per IS: 4736-1986 (with up to date ammendements) . | BI01010001010000000000000515BI0100001142 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
12.01 | 80 mm dia Kunihar Block | BI01010001010000000000000515BI0100001143 | 4097 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12.02 | 80 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001144 | 6900 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12.03 | 100 mm dia Kunihar Block | BI01010001010000000000000515BI0100001145 | 5668 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12.04 | 100 mm dia Nalagarh block | BI01010001010000000000000515BI0100001146 | 5756 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12.05 | 125 mm dia Kunihar Block | BI01010001010000000000000515BI0100001147 | 129 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12.06 | 125 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001148 | 111 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12.07 | 150 mm dia Kunihar Block | BI01010001010000000000000515BI0100001149 | 23 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13 | Providing, laying, jointing and testing of MS pipe, thickness 4.8 mm, MSERW flanged / Butt welded joints by considering three layers pipes including cost of bends complete as per GMSERW Pipe conforming to IS / ISO: 3183-2007 of following grade & wall thicknesses as per dimensions, weights and test pressure mentioned below in a random length of 4 to 7 meters. The M.S.flanges are to be provided on each joint as per required table conforming to IS: 6392-1971 and welding of flanges with electrodes as per relevants codes including required number & size of nuts and bolts & gasket sheet not less than 3mm thickness as per relevants codes. The welding of flanges to be done on both faces in two layers to make the joints leak proof and to entire satisfaction of the Engineer-in-charge. The laying of pipe should be conformed to IS: 5822-1994. (Earth work in trenches to be measured and paid for separately). The pipe shall be galvanising with zinc coating conforming to IS: 4736-1986. of following diameters:- | BI01010001010000000000000515BI0100001150 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
13.01 | 125 mm dia 4.8 mm thick with Flange Table-5 Kunihar Block | BI01010001010000000000000515BI0100001151 | 2301 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13.02 | 200 mm dia 4.8 mm thick with Flange Table-5 Nalagarh Block | BI01010001010000000000000515BI0100001152 | 1846 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13.03 | 300 mm dia 4.8 mm thick with Flange Table-5 Nalagarh Block | BI01010001010000000000000515BI0100001153 | 2820 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14 | Providing and fixing double flanged cast iron sluice valve of following dia of approved make of JSV to gravity main confirming to BIS: 780-1984 Class PN 1.00 having seat pressureof 10.20 Kg/cm² with M.SFlanges of table -5 with up to date ammendements. | BI01010001010000000000000515BI0100001154 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
14.01 | 80 mm dia Kunihar Block | BI01010001010000000000000515BI0100001155 | 9 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.02 | 80 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001156 | 13 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.03 | 100 mm dia Kunihar Block | BI01010001010000000000000515BI0100001157 | 14 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.04 | 100 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001158 | 13 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.05 | 125 mm dia Kunihar Block | BI01010001010000000000000515BI0100001159 | 9 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.06 | 125 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001160 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.07 | 150 mm dia Kunihar Block | BI01010001010000000000000515BI0100001161 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.08 | 200 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001162 | 4 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.09 | 300 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001163 | 6 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
15 | Providing and fixing screwed/flanged CI air valve (Single/double ball type) of approved make of JSV conforming to BIS-1452-1990 with upto date ammendments as per class PN-1.0 withstanding a seat pressure 15 Kg/cm2 in rising main within all leads and lifts. 25mm Dia.Kunihar Block | BI01010001010000000000000515BI0100001164 | 18 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
16 | Providing and fixing screwed/flanged CI air valve (Single/double ball type) of approved make of JSV conforming to BIS-1452-1990 with upto date ammendments as per class PN-1.0 withstanding a seat pressure 15 Kg/cm2 in rising main within all leads and lifts. 25mm Dia. Nalagarh Block | BI01010001010000000000000515BI0100001165 | 18 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
17 | Providing and fixing double flanged cast iron Scour valve of following dia of approved make of JSV to gravity main confirming to BIS: 780-1984 Class PN 1.00 having seat pressureof 10.20 Kg/cm² with M.SFlanges of table -5 with up to date ammendements. | BI01010001010000000000000515BI0100001166 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
17.01 | 80 mm dia Kunihar Block | BI01010001010000000000000515BI0100001167 | 25 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
17.02 | 80 mm dia Nalagarh Block | BI01010001010000000000000515BI0100001168 | 27 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Construction of Anchor Block at every in CC 1:1.5:3 (1 cement :1.5 sand :3 graded stone add 20 mm NS) i/c cost of Excavation , form work , C.C work, and reinforcement & curing complete of tentative size 1.50m x 1.50m x 2.00m to provide support to rising main pipe after every 50 m length complete as per direction and to the entire satisfaction of Engineer -in-Charge with in all leads and lifts. (The RD wise structural design shall got approved from the competent autrhority prior to construction of Thrust/Anchor blocks). | BI01010001010000000000000515BI0100001169 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
18.01 | Kunihar Block | BI01010001010000000000000515BI0100001170 | 50 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
18.02 | Nalagarh Block | BI01010001010000000000000515BI0100001171 | 70 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) RCC Circular under ground/partial under ground storage reservoirs as per capacity given below at various stages/sites including excavation in foundation in all kinds of soil. including PCC (1:3:6) in foundation and M:30 design mix in bottom slab/raft ,walls and beams. And RCC (1:1.5:3) in roof slab/dome with provision of inspection path around the dome with all alied Civil Works such as c/o chamber for valves, refilling and disposing of surplus excavated earth with in all leads and lifts. The job also includes providing lowering, laying, erecting, hoisting and jointing of pipe assembly for inlet, outlet, overflow and scour pipe with bye pass arrangement consisting of GI / MS pipes special and valves of required classes and dia and all other accessories required such as MS ladders inside and outside, CI cowl type ventilator, SFRC manhole covers with frames of heavy duty with proper locking arrangement, water level indicator. The tanks shall be hydraulically tested for water tightness, All works shall be conforming to relevant IS code. The cost of valves, be included in the rates of tanks .complete in all respects to the entire satisfaction of the Engineer-in-charge. Refer Data Sheet No-5 | BI01010001010000000000000515BI0100001172 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
19.01 | 1.0 Lakh Litre Capacity Kunihar Block | BI01010001010000000000000515BI0100001173 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.02 | 1.5 Lakh Litre Capacity Kunihar Block | BI01010001010000000000000515BI0100001174 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.03 | 2.0 Lakh Litre Capacity Kunihar Block | BI01010001010000000000000515BI0100001175 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.04 | 3.0 Lakh Litre Capacity Kunihar Block | BI01010001010000000000000515BI0100001176 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.05 | 1.0 Lakh Litre Capacity Nalagarh Block | BI01010001010000000000000515BI0100001177 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.06 | 2.0 Lakh Litre Capacity Nalagarh Block | BI01010001010000000000000515BI0100001178 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.07 | 3.0 Lakh Litre Capacity Nalagarh Block | BI01010001010000000000000515BI0100001179 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level. | BI01010001010000000000000515BI0100001180 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
20.01 | Kunihar Block | BI01010001010000000000000515BI0100001181 | 54 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20.02 | Nalagarh Block | BI01010001010000000000000515BI0100001182 | 114 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Pumping Machinery | BI01010001010000000000000515BI0100001183 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
22 | SUBMERSIBLE PUMP SETS- Supply Installation Testing & Commissioning of submersible pumping set of KSB/ Crompton/ Kirloskar/ BS/ Calama make conforming to latest relevant BIS Code 8034:1976. The impeller of pump shall be directly mounted on extended submersible squirrel cage motor shaft conforming to BIS 9283-1979 with up to date amendments, totally dust and weather proof with detach able pump casing for easy inspection with double mechanical seal, grease/ oil lubricated bearings and provided with stainless steel thrust bearing plate to withstand vertical loads with minimum wear and tear, It should be fitted with device to take up expansion of water on heating of motor & suitable for operation on 415V ± 10%, 3 Phase 50 Hz AC supply. The pump motor shall be VFD duty and its power should be at least 10% in excess of maximum power required by the pump in complete operating range with mounting stand/ duck foot bend, steel guide wire with mounting hook, lowering chain and standard accessories as supplied by the manufacturers complete, suitable for fulfilling the following requirements:- including Pump sets (working ), necessary piping, electro-mechanical flowmeter and control valves along with electrical works including indoor & outdoor HT/LT switchboards/ PCC, Soft Starter Cubicle(VFD) with suitable bypass arrangement, HT/LT Cabling system complete with end terminations, cable trays & accessories, Earthing system with maintenance free earth electrodes, 415/ 230V small power distribution boards, local push button stations, Junction Boxes, Power/ Welding receptacles and its associated wiring/ cabling etc.,as per requirement of pumping machinery; complete work inclusive of all taxes, insurance, transportation, freight charges, inspection charges, loading, unloading, conveyance to Departmental stores/ site, stacking, etc. including specials and wastage etc.; complete as per Tender Specifications, technical data Sheets and instruction of Engineer in charge. | BI01010001010000000000000515BI0100001184 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
22.01 | For Tube well at Beli khol LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 7 LPS vi) Static Head in meters _14 mts. vii) Duty/Total head in Mts= 25 mts viii) Length of R/Main 34.00mts ix) Dia of R/Main=100 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 7 LPS each with 25 m head | BI01010001010000000000000515BI0100001185 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
22.02 | For Tube well at Palli LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 8.5 LPS vi) Static Head in meters _14 mts. vii) Duty/Total head in Mts= 20 mts viii) Length of R/Main 31.00mts ix) Dia of R/Main=125 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 8.5 LPS each with 25 m head | BI01010001010000000000000515BI0100001186 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | SUBMERSIBLE PUMP SETS- Supply Installation Testing & Commissioning of submersible pumping set of KSB/ Crompton/ Kirloskar/ BS/ Calama make conforming to latest relevant BIS Code 8034:1976. The impeller of pump shall be directly mounted on extended submersible squirrel cage motor shaft conforming to BIS 9283-1979 with up to date amendments, totally dust and weather proof with detach able pump casing for easy inspection with double mechanical seal, grease/ oil lubricated bearings and provided with stainless steel thrust bearing plate to withstand vertical loads with minimum wear and tear, It should be fitted with device to take up expansion of water on heating of motor & suitable for operation on 415V ± 10%, 3 Phase 50 Hz AC supply. The pump motor shall be VFD duty and its power should be at least 10% in excess of maximum power required by the pump in complete operating range with mounting stand/ duck foot bend, steel guide wire with mounting hook, lowering chain and standard accessories as supplied by the manufacturers complete, suitable for fulfilling the following requirements:- including Pump sets (working ), necessary piping, eletro-mechanical flow meter and control valves along with electrical works including indoor & outdoor HT/LT switchboards/ PCC, Soft Starter Cubicle(VFD) with suitable bypass arrangement, HT/LT Cabling system complete with end terminations, cable trays & accessories, Earthing system with maintenance free earth electrodes, 415/ 230V small power distribution boards, local push button stations, Junction Boxes, Power/ Welding receptacles and its associated wiring/ cabling etc.,as per requirement of pumping machinery; complete work inclusive of all taxes, insurance, transportation, freight charges, inspection charges, loading, unloading, conveyance to Departmental stores/ site, stacking, etc. including specials and wastage etc.; complete as per Tender Specifications, technical data Sheets and instruction of Engineer in charge. | BI01010001010000000000000515BI0100001187 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
23.01 | From Intake Well to Desilting tank at Jailang LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 7.5 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 30 mts viii) Length of R/Main 24.00mts ix) Dia of R/Main=100 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 7.5 LPS each with 30 m head | BI01010001010000000000000515BI0100001188 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23.02 | From P. Well to Desilting tank at Datti LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 8.6 LPS vi) Static Head in meters _12 mts. vii) Duty/Total head in Mts= 20 mts viii) Length of R/Main13.00mts ix) Dia of R/Main=125 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 41 LPS each with 20 m head | BI01010001010000000000000515BI0100001189 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
23.03 | From P. Well to Desilting tank at Daseran LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 15.8 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 30 mts viii) Length of R/Main 2301 mts ix) Dia of R/Main=150 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 15.8 LPS each with 30 m head | BI01010001010000000000000515BI0100001190 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23.04 | From P. Well to Desilting tank at Pajeena LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 8.8 LPS vi) Static Head in meters _23 mts. vii) Duty/Total head in Mts= 35 mts viii) Length of R/Main 26 mts ix) Dia of R/Main=100 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 8.8 LPS each with 35 m head | BI01010001010000000000000515BI0100001191 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
23.05 | From P. Well to Desilting tank at Chunad LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 13.2 LPS vi) Static Head in meters _65 mts. vii) Duty/Total head in Mts= 75 mts viii) Length of R/Main 27 mts ix) Dia of R/Main=125 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 13.2 LPS each with 75 m head | BI01010001010000000000000515BI0100001192 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
23.06 | From Intake Well to Desilting tank at Doli LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 11.6 LPS vi) Static Head in meters _21 mts. vii) Duty/Total head in Mts= 30 mts viii) Length of R/Main 15 mts ix) Dia of R/Main=125 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 11.6 LPS each with 30 m head | BI01010001010000000000000515BI0100001193 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
23.07 | From P. Well to Desilting tank at Batiakh LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 34.32 LPS vi) Static Head in meters _13 mts. vii) Duty/Total head in Mts= 20 mts viii) Length of R/Main 1846 mts ix) Dia of R/Main=200 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 34.32 LPS each with 30 m head | BI01010001010000000000000515BI0100001194 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
23.08 | From P. Well to Desilting tank at Sour LIS i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 43 LPS vi) Static Head in meters _157 mts. vii) Duty/Total head in Mts= 180 mts viii) Length of R/Main 1846 mts ix) Dia of R/Main=300 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .3 sets (1 as stand by) of 85 LPS each with 180 m head | BI01010001010000000000000515BI0100001195 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24 | CENTRIFUGAL PUMP SETS- Supply Installation Testing & Commissioning ) of horizontal spindle, horizontal/redial split casing/end suction(Back-pull out arrangements) single/double/multi stage star rated centrifugal pump or combination of pumps, of recommended make such as Mather and Platt/KSB/Kirloskar as per BIS 1520-1980 with up to date amendments, read with IS:9137-1978 or latest edition suitable for lifting water for under mentioned characteristics with bronze, impellers/ priming funnels, casing ring and shaft sleeves of bronze, shaft of steel grade 45C8/ EN8 with cast iron casing coupled directly through a flexible coupling on a common MS Base Plate to squirrel cage TEFC Energy efficient motors (Conforming to energy efficiency code IE3 or higher ) of standard make such as Kirloskar / BHEL / CG POWER / Siemens / ABB / Marathon and suitable for operation on 415V ± 10%, 50 Hz., 3 phase AC electric supply. The pump motor shall be VFD duty and its power should be at least +10% in excess of the maximum power required by the pump/pumps in the operation range of (+) 10% and (-)15% of the duty point head. The motor/motors as per IS 12615 : 2011 with up to date amendments. The scope shall also include necessary piping for suction, delivery & common header and eletro-magnetic flowmeter, along with electrical works including indoor & outdoor HT/LT switchboards/ PCC, Soft Starter Cubicle(VFD) with suitable bypass arrangement, HT/LT Cabling system complete with end terminations, cable trays & accessories, Earthing system with maintenance free earth electrodes, 415/ 230V small power distribution boards, local push button stations, Junction Boxes, Power/ Welding receptacles and its associated wiring/ cabling etc. as per requirement of following pumping machinery; Complete work inclusive of all taxes, transportation, freight charges, inspection charges, loading, unloading, conveyance to Departmental stores / site, stacking, etc. including specials and wastage etc. It shall include providing and fixing of C.I/C.S Sluice valves of approved make and appropriate class to resist the design pressure and complete as per Tender Specifications and instruction of Engineer in charge. | BI01010001010000000000000515BI0100001196 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
24.01 | At Jailang LIS 2 sets (1 as stand by) of 3.5 LPS each with 155 m Total head , 2900 RPM ,with 16 Hours Pumping | BI01010001010000000000000515BI0100001197 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24.02 | At Datti LIS 2 sets (1 as stand by) of 5.0 LPS each with 25 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001198 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.03 | At Daseran LIS 2 sets (1 as stand by) of 12.20 LPS each with 250 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001199 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24.04 | At Giana LIS 2 sets (1 as stand by) of 2.5 LPS each with 135 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001200 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.05 | At Pajeena LIS 2 sets (1 as stand by) of 5.2 LPS each with 75 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001201 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.06 | At Chunad LIS 2 sets (1 as stand by) of 6.0 LPS each with 165 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001202 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.07 | At Doli LIS 2 sets (1 as stand by) of 6.2 LPS each with 225 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001203 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.08 | At Batiakh LIS 3 sets (1 as stand by) of 34.32 LPS each with 195 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001204 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.09 | At Sour LIS 3 sets (1 as stand by) of 43 LPS each with 120 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001205 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.1 | At Palli LIS 2 sets (1 as stand by) of 3.2 LPS each with 110 m Total head & 2 sets (1 as stand by) of 1.3 LPS each with 90 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001206 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
24.11 | At Beli Khol 1 LIS 2 sets (1 as stand by) of 3.7 LPS each with 50 m Total head , 2900 RPM with 16 Hours Pumping | BI01010001010000000000000515BI0100001207 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
25 | INSTRUMENTATION, CONTROL & AUTOMATION WORK-Supply, installation, testing, integration, programming & commissioning of Instrumentation, Control & Automation system for Lift Irrigation including Level Transmitter with display, Level Indicator, Level Switch, Pressure Transmitter, Gauges, Actuated Valves, Flow Meter, micro PLC based Remote Terminal Unit (RTU) along with panel mounted 10” HMI, UPS, SPD, Instrumentation Cables, Cable Trays, Earthing system etc., necessary gateways with SIM card for remote data communication and all other ancillary works and accessories required to make the system fully functional as per user requirement . Scope includes for 13 new schemes ( LIS Ser-Delag, LIS Sai, LIS Giana, LIS Pajeena, LIS Datti, LIS Daseran, LIS Palli, LIS Bheli koli-1, LIS Sour, LIS Doli, LIS Batiakh, LIS Chunad and LIS Jailang ) Refer Data Sheet No-6 | BI01010001010000000000000515BI0100001208 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information