## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Executive Engineer Cum Project Manager Jal Shakti Vibhag, Division Nahan, Himachal Pradesh
Name of Work: Providing Irrigation Facility under HP SHIVA Project for Nahan and Paonta Sahib Blocks, District Sirmour (Himachal Pradesh)- Package 2
Contract No: HPSHIVA-E-Tender-CWJ/IRG/SMR-01/2022-23/02:- 16284-334 dated 21-01-2023 Opened on 24-02-2023
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT including Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Civil Work | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2 | RCC Check Dam : Designing, Constructing, Testing & Commissioning ( to be approved by the competent authority) of RCC Check Dam, as per technical specification given in bid document, complete in all respects to the entire satisfaction of the Engineer-in-charge. | BI01010001010000000000000515BI0100001113 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.1 | 15 m length and 3.85 m At LIS Dungi Sher, LIS Rama, LIS Khairi Chandan 1&2 and LIS Judag | BI01010001010000000000000515BI0100001114 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.2 | 15 m length and 3,85 m height At LIS Khara | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.3 | 15 m length and 3.85 m height At LIS Bajari 1&2 | BI01010001010000000000000515BI0100001116 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | RCC Intake Structure :- Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) of RCC intake Structure as per drawings, having RCC structure, Roofing with RCC slab, allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling ,MCB DBs,receptacle system & accessories etc., Walk way/ passage CI Rungs inside the structure from top to bottom and steel stair case from ground level to top of intake with connecting path having suitable capacity crane/ hoist arrangement for handling of pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge. for . Refer Data Sheet No-1 | BI01010001010000000000000515BI0100001117 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4 | Tube Well :- Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) of Tube Well as per drawings including allied electrication work including lighting fixtures, fans, street / area lighting using poles, associated wiring/ cabling, MCB DBs & switchboards, receptacle system & accessories etc., mono rail with chain pulley arrangement of suitable capacity for lowering/ lifting the pumping machinery complete in all respects to the entire satisfaction of the Engineer-in-charge.At LIS Fatehpur , LIS Upper Buddi (2 Nos), LIS Puruwala, LIS Gyaniwala | BI01010001010000000000000515BI0100001118 | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5 | PUMP HOUSE:- Designing, Constructing, Testing & Commissioning of Pump House & Chowkidar Room at following locations including all allied Civil Works, Electrical Works including lighting fixtures, fans, street / area lighting using poles, associated cabling/ wiring, MCB DBs, receptacle system & accessories etc., Sanitary Work, Site Development, Cutting/ Excavation in all kinds of soils, c/o PCC/ RCC Retaining walls, Breast walls, Toilets, Septic Tanks, External Solar powered Street lighting, External landscaping, Fire Fighting arrangement, Building Lightning Protection System (where applicable), Gantry Crane, dewatering etc complete as directed by engineer in charge The rates quoted by the contractor shall be for the complete work. All ancillary works and accessories required to make the system fully functional shall be included in the cost of work. Nothing extra shall be paid on this account. Pump house of 35.00 Sqm. Area Refer Data Sheet No-2 | BI01010001010000000000000515BI0100001119 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
5.1 | At LIS Bajari 1&2, LIS Bhogapur simbalwhala, LIS Budriyon, LIS Dungi Sher, LIS Goant, LIS Khairi Chandan 1&2, LIS Rama and LIS Jugad | BI01010001010000000000000515BI0100001120 | 8 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.2 | At LIS Fatehpur, LIS Killour, LIS Upper Buddi, LIS Khara, LIS Puruwala and LIS Gyaniwala | BI01010001010000000000000515BI0100001121 | 6 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6 | Designing, Constructing, Testing & Commissioning of Desilting tank including civil work, Necessary valves & fittings, tube settler media etc. complete in all respect as per the drawings & technical specification.for the followings size- Refer Data Sheet No-3 | BI01010001010000000000000515BI0100001122 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
6.1 | 13 KL Capacity at LIS Rama | BI01010001010000000000000515BI0100001123 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
6.2 | 14 KL Capacity at LIS Khara | BI01010001010000000000000515BI0100001124 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.3 | 20 KL Capacity at LIS Dungi Sher and LIS Goant | BI01010001010000000000000515BI0100001125 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6.4 | 24 KL Capacity at LIS Bajari 1&2 and LIS Judag | BI01010001010000000000000515BI0100001126 | 2 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6.5 | 32 KL Capacity at LIS Bhogapur | BI01010001010000000000000515BI0100001127 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.6 | 37 KL Capacity at LIS Killour | BI01010001010000000000000515BI0100001128 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6.7 | 44 KL Capacity at LIS Khairi Chandan 1&2 | BI01010001010000000000000515BI0100001129 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | Designing, Constructing, Testing & Commissioning of Sump well including civil work, Necessary valves & fittings etc. complete in all respect as per the drawings & technical specification.for the followings size- | BI01010001010000000000000515BI0100001130 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
7.01 | 9 KL Capacity at LIS Rama | BI01010001010000000000000515BI0100001131 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
7.02 | 9 KL Capacity at LIS Fatehpur | BI01010001010000000000000515BI0100001132 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.03 | 11 KL Capacity at LIS Goant | BI01010001010000000000000515BI0100001133 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.04 | 13 KL Capacity at LIS Khara | BI01010001010000000000000515BI0100001134 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.05 | 14 KL Capacity at LIS Dungi Sher | BI01010001010000000000000515BI0100001135 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
7.06 | 15 KL Capacity at LIS Gyaniwala | BI01010001010000000000000515BI0100001136 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.07 | 17 KL Capacity LIS Judag | BI01010001010000000000000515BI0100001137 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.08 | 18 KL Capacity at LIS Puruwala | BI01010001010000000000000515BI0100001138 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.09 | 20 KL Capacity at LIS Bajari 1&2 | BI01010001010000000000000515BI0100001139 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.1 | 21 KL Capacity at LIS Budriyon | BI01010001010000000000000515BI0100001140 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.11 | 25 KL Capacity LIS Bhogapur | BI01010001010000000000000515BI0100001141 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
7.12 | 28 KL Capacity at LIS Upper Buddi | BI01010001010000000000000515BI0100001142 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.13 | 30 KL Capacity at LIS Killour | BI01010001010000000000000515BI0100001143 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.14 | 38 KL Capacity at LIS Khairi Chandan 1&2 | BI01010001010000000000000515BI0100001144 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8 | Excavation in foundation, trenches (for pipes & pits) upto all depths in all classification of earth work such as pick work, jumper work, saturated soil including bailing and pumping out water, blasting soft/ hard rock or chieselling soft/hard rock where blasting is prohibited in all lifts including trimming and dressing of sides, leveling of beds to correct grade i/c shoring /strutting , planking, timbering & dewatering wherever required, stacking the useable & unuseable material /soil separately & after laying jointing & testing of pipes, returning the useable soil in trenches in 15 cm layers including consolidating of such deposoited layer by ramming & watering & then disposing of all surplus excavated soil /unusable material as directed with in all leads & lifts Excluding restoration metalled surfaces to its original condition( Will be paid Separately) & including cost of diversion for traffic, night signals, fixing caution boards, crossing over trenches for access to houses, fencing etc. complete in all respects with in all leads & lifts as per directions of Engineer-in-charge. | BI01010001010000000000000515BI0100001145 | 12857.93 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9 | Providing ,Laying,jointing & testing of Galvanised Mild steel tube with flange / Butt welding of approved make or by JSV Deptt (list attached) conforming to BIS 1239-2004 ( with upto date ammendements ) of following diameter and class including all specials and fittings as required complete as per actual site condition with in all leads and lifts as per the direction and to the entire satisfaction of Engineer-in Charge. The pipe shall be factory galvanized as per IS: 4736-1986 (with up to date ammendements) . | BI01010001010000000000000515BI0100001146 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
9.1 | 80 mm dia (Medium Class) Paonta Sahib Block | BI01010001010000000000000515BI0100001147 | 2725 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.2 | 80 mm dia (Medium Class) Nahan Block | BI01010001010000000000000515BI0100001148 | 13811 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.3 | 100 mm dia (Medium Class) | BI01010001010000000000000515BI0100001149 | 4431 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.4 | 150 mm dia (Medium Class) | BI01010001010000000000000515BI0100001150 | 380 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Providing and fixing double flanged cast iron sluice valve of following dia of approved make of JSV to gravity main confirming to BIS: 780-1984 Class PN 1.00 having seat pressureof 10.20 Kg/cm² with M.SFlanges of table -5 with up to date ammendements. | BI01010001010000000000000515BI0100001151 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
10.1 | 80 mm dia Paonta Sahib Block | BI01010001010000000000000515BI0100001152 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.2 | 80 mm dia Nahan Block | BI01010001010000000000000515BI0100001153 | 20 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.3 | 100 mm dia | BI01010001010000000000000515BI0100001154 | 5 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.4 | 150 mm dia | BI01010001010000000000000515BI0100001155 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11 | Providing and fixing screwed/flanged CI air valve (Single/double ball type) of approved make of JSV conforming to BIS-1452-1990 with upto date ammendments as per class PN-1.0 withstanding a seat pressure 15 Kg/cm2 in rising main within all leads and lifts. 25mm Dia. Paonta Sahib Block | BI01010001010000000000000515BI0100001156 | 13 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12 | Providing and fixing screwed/flanged CI air valve (Single/double ball type) of approved make of JSV conforming to BIS-1452-1990 with upto date ammendments as per class PN-1.0 withstanding a seat pressure 15 Kg/cm2 in rising main within all leads and lifts. 25mm Dia. Nahan Block | BI01010001010000000000000515BI0100001157 | 75 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13 | Construction of Anchor Block at every in CC 1:1.5:3 (1 cement :1.5 sand :3 graded stone add 20 mm NS) i/c cost of Excavation , form work , C.C work, and reinforcement & curing complete of tentative size 1.50m x 1.50m x 2.00m to provide support to rising main pipe after every 50 m length complete as per direction and to the entire satisfaction of Engineer -in-Charge with in all leads and lifts. (The RD wise structural design shall got approved from the competent autrhority prior to construction of Thrust/Anchor blocks). Paonta Sahib Block | BI01010001010000000000000515BI0100001158 | 13 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14 | Construction of Anchor Block at every in CC 1:1.5:3 (1 cement :1.5 sand :3 graded stone add 20 mm NS) i/c cost of Excavation , form work , C.C work, and reinforcement & curing complete of tentative size 1.50m x 1.50m x 2.00m to provide support to rising main pipe after every 50 m length complete as per direction and to the entire satisfaction of Engineer -in-Charge with in all leads and lifts. (The RD wise structural design shall got approved from the competent autrhority prior to construction of Thrust/Anchor blocks). Nahan Block | BI01010001010000000000000515BI0100001159 | 71 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
15 | Designing, Constructing, Testing & Commissioning (to be approved by the competent authority) RCC Circular under ground/partial under ground storage reservoirs as per capacity given below at various stages/sites including excavation in foundation in all kinds of soil. including PCC (1:3:6) in foundation and M:30 design mix in bottom slab/raft ,walls and beams. And RCC (1:1.5:3) in roof slab/dome with provision of inspection path around the dome with all alied Civil Works such as c/o chamber for valves, refilling and disposing of surplus excavated earth with in all leads and lifts. The job also includes providing lowering, laying, erecting, hoisting and jointing of pipe assembly for inlet, outlet, overflow and scour pipe with bye pass arrangement consisting of GI / MS pipes special and valves of required classes and dia and all other accessories required such as MS ladders inside and outside, CI cowl type ventilator, SFRC manhole covers with frames of heavy duty with proper locking arrangement, water level indicator. The tanks shall be hydraulically tested for water tightness, All works shall be conforming to relevant IS code. The cost of valves, be included in the rates of tanks .complete in all respects to the entire satisfaction of the Engineer-in-charge. Refer Data Sheet No-4 | BI01010001010000000000000515BI0100001160 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
15.1 | 200 KL | BI01010001010000000000000515BI0100001161 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
15.2 | 300 KL | BI01010001010000000000000515BI0100001162 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
16 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with :Paonta Sahib | BI01010001010000000000000515BI0100001163 | 9 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with : Nahan Block | BI01010001010000000000000515BI0100001164 | 99 | Cum | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Pumping Machinery | BI01010001010000000000000515BI0100001165 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
19 | SUBMERSIBLE PUMP SETS- Supply Installation Testing & Commissioning of submersible pumping set of KSB/ Crompton/ Kirloskar/ BS/ Calama make conforming to latest relevant BIS Code 8034:1976. The impeller of pump shall be directly mounted on extended submersible squirrel cage motor shaft conforming to BIS 9283-1979 with up to date amendments, totally dust and weather proof with detach able pump casing for easy inspection with double mechanical seal, grease/ oil lubricated bearings and provided with stainless steel thrust bearing plate to withstand vertical loads with minimum wear and tear, It should be fitted with device to take up expansion of water on heating of motor & suitable for operation on 415V ± 10%, 3 Phase 50 Hz AC supply. The pump motor shall be VFD duty and its power should be at least 10% in excess of maximum power required by the pump in complete operating range with mounting stand/ duck foot bend, steel guide wire with mounting hook, lowering chain and standard accessories as supplied by the manufacturers complete, suitable for fulfilling the following requirements:- including Pump sets (working ), necessary piping, eletro-mechanical flow meter and control valves along with electrical works including indoor & outdoor HT/LT switchboards/ PCC, Soft Starter Cubicle(VFD) with suitable bypass arrangement, HT/LT Cabling system complete with end terminations, cable trays & accessories, Earthing system with maintenance free earth electrodes, 415/ 230V small power distribution boards, local push button stations, Junction Boxes, Power/ Welding receptacles and its associated wiring/ cabling etc.,as per requirement of pumping machinery; complete work inclusive of all taxes, insurance, transportation, freight charges, inspection charges, loading, unloading, conveyance to Departmental stores/ site, stacking, etc. including specials and wastage etc.; complete as per Tender Specifications, technical data Sheets and instruction of Engineer in charge. | BI01010001010000000000000515BI0100001166 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
19.01 | From Intake Well to Desilting tank at LIS Killour i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 8 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 22 mts viii) Length of R/Main 300.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 8 LPS each with 22 m head | BI01010001010000000000000515BI0100001167 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.02 | From Check Dam to Desilting tank at LIS Khara i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 3.3 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 22 mts viii) Length of R/Main130.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 3.3 LPS each with 22 m head | BI01010001010000000000000515BI0100001168 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.03 | From Check Dam to Desilting tank at LIS Dungi Sher i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 3.54 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 22 mts viii) Length of R/Main130.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 3.54 LPS each with 22 m head | BI01010001010000000000000515BI0100001169 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.04 | From Check Dam to Desilting tank at LIS Bajari 1&2 i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 5.11 LPS vi) Static Head in meters _23 mts. vii) Duty/Total head in Mts= 25 mts viii) Length of R/Main110.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 5.11 LPS each with 25 m head | BI01010001010000000000000515BI0100001170 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.05 | From Check Dam to Desilting tank at LIS Rama i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 2.51 LPS vi) Static Head in meters _21 mts. vii) Duty/Total head in Mts= 23 mts viii) Length of R/Main130.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 2.51 LPS each with 23 m head | BI01010001010000000000000515BI0100001171 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.06 | From Check Dam to Desilting tank at LIS Jungle Bhood- Simbhalwala & Bhogpur i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 6.76 LPS vi) Static Head in meters _28 mts. vii) Duty/Total head in Mts= 30 mts viii) Length of R/Main150.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 6.76 LPS each with 30 m head | BI01010001010000000000000515BI0100001172 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.07 | From Check Dam to Desilting tank at LIS Khairi Chandan 1&2 i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 10.31 LPS vi) Static Head in meters _30 mts. vii) Duty/Total head in Mts= 32 mts viii) Length of R/Main100.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 10.31 LPS each with 32 m head | BI01010001010000000000000515BI0100001173 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.08 | From Check Dam to Desilting tank at LIS Judag i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 4.61 LPS vi) Static Head in meters _24 mts. vii) Duty/Total head in Mts= 26 mts viii) Length of R/Main 80.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 4.61 LPS each with 26 m head | BI01010001010000000000000515BI0100001174 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.09 | From Check Dam to Desilting tank at LIS Goant i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Raw Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 2.92 LPS vi) Static Head in meters _21 mts. vii) Duty/Total head in Mts= 23 mts viii) Length of R/Main 200.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 2.92 LPS each with 23 m head | BI01010001010000000000000515BI0100001175 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.1 | For Tube well at LIS Budriyon i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 6 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 22 mts viii) Length of R/Main 34.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 6 LPS each with 22 m head | BI01010001010000000000000515BI0100001176 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.11 | For Tube well at LIS Fatehpur i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 2.5 LPS vi) Static Head in meters _20 mts. vii) Duty/Total head in Mts= 22 mts viii) Length of R/Main 150.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. .2 sets (1 as stand by) of 2.5 LPS each with 22 m head | BI01010001010000000000000515BI0100001177 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.12 | For Tube well at LIS Upper Bhuddi i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 8 LPS vi) Static Head in meters _18 mts. vii) Duty/Total head in Mts= 20 mts viii) Length of R/Main 200.00mts ix) Dia of R/Main=100 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. 2 sets (1 as stand by) of 8 LPS each with 20 m head | BI01010001010000000000000515BI0100001178 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.13 | For Tube well at LIS Puruwala i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 5 LPS vi) Static Head in meters _18 mts. vii) Duty/Total head in Mts= 20 mts viii) Length of R/Main 140.00mts ix) Dia of R/Main=100 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. 2 sets (1 as stand by) of 5 LPS each with 20 m head | BI01010001010000000000000515BI0100001179 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.14 | For Tube well at LIS Gyayaniwala i) Rated Voltage :- 415V ± 10% iii) Charactrstics of water:-Under Ground Water) Temperature _20_ °C, b) Turbidity upto 100 NTU, c) pH 6.5 to 8 d ) Total solids :-600mg/litre, v) Discharge at Duty Point= 4 LPS vi) Static Head in meters _19 mts. vii) Duty/Total head in Mts= 21 mts viii) Length of R/Main 100.00mts ix) Dia of R/Main=80 mm x) Pumping hours per day- 16 hours xi) Limits of pump operation (-) 15% to (+) 10% of Total head at duty point xii) HP of motor /Drive unit ---, Power absorbed or Required BHP at (-) 15% of Duty head or BHP with margins/multiplying factor at duty point & (+) 10% head , whichever is higher i.e Upto 2 HP = 1.5 , 2 to 5 HP = 1.4, 5 to 10 HP = 1.3 , 10 to 20 HP = 1.2 , 20 to100 HP = 1.15, Above 100 HP=1.10 xiii) Efficiency at duty point Minimum 60% xiv) R.P.M.of Pumping set -2900, xv) Test Run-24 hours continueously for 7 days. 2 sets (1 as stand by) of 4 LPS each with 21 m head | BI01010001010000000000000515BI0100001180 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | CENTRIFUGAL PUMP SETS- Supply Installation Testing & Commissioning ) of horizontal spindle, horizontal/redial split casing/end suction(Back-pull out arrangements) single/double/multi stage star rated centrifugal pump or combination of pumps, of recommended make such as Mather and Platt/KSB/Kirloskar as per BIS 1520-1980 with up to date amendments, read with IS:9137-1978 or latest edition suitable for lifting water for under mentioned characteristics with bronze, impellers/ priming funnels, casing ring and shaft sleeves of bronze, shaft of steel grade 45C8/ EN8 with cast iron casing coupled directly through a flexible coupling on a common MS Base Plate to squirrel cage TEFC Energy efficient motors (Conforming to energy efficiency code IE3 or higher ) of standard make such as Kirloskar / BHEL / CG POWER / Siemens / ABB / Marathon and suitable for operation on 415V ± 10%, 50 Hz., 3 phase AC electric supply. The pump motor shall be VFD duty and its power should be at least +10% in excess of the maximum power required by the pump/pumps in the operation range of (+) 10% and (-)15% of the duty point head. The motor/motors as per IS 12615 : 2011 with up to date amendments. The scope shall also include necessary piping for suction, delivery & common header and eletro-magnetic flowmeter, along with electrical works including indoor & outdoor HT/LT switchboards/ PCC, Soft Starter Cubicle(VFD) with suitable bypass arrangement, HT/LT Cabling system complete with end terminations, cable trays & accessories, Earthing system with maintenance free earth electrodes, 415/ 230V small power distribution boards, local push button stations, Junction Boxes, Power/ Welding receptacles and its associated wiring/ cabling etc. as per requirement of following pumping machinery; Complete work inclusive of all taxes, transportation, freight charges, inspection charges, loading, unloading, conveyance to Departmental stores / site, stacking, etc. including specials and wastage etc. It shall include providing and fixing of C.I/C.S Sluice valves of approved make and appropriate class to resist the design pressure and complete as per Tender Specifications and instruction of Engineer in charge. | BI01010001010000000000000515BI0100001181 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
20.01 | At LIS Dungi sher 2 sets (1 as stand by) of 4 LPS each with 144 m Total head ,at 1450 RPM, ,with 16 Hours Pumping | BI01010001010000000000000515BI0100001182 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20.02 | At LIS Bajari 1&2 2 sets (1 as stand by) of 3.4 LPS each with 64 m Total head ,at 1450 RPM, with 16 Hours Pumping and another 2 sets (1 as stand by) of 2 LPS each with 33 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001183 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.03 | At LIS Rama 2 sets (1 as stand by) of 2.51 LPS each with 245 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001184 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.04 | At LIS Jungle Bhood- Simbhalwala & Bhogpur 2 sets (1 as stand by) of 7 LPS each with 135 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001185 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.05 | At LIS Khairi Chandan 1&2 2 sets (1 as stand by) of 5.31 LPS each with 274 m Total head ,at 1450 RPM, with 16 Hours Pumping and another 2 sets (1 as stand by) of 5.10 LPS each with 92 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001186 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.06 | At LIS Judag 2 sets (1 as stand by) of 4.44 LPS each with 125 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001187 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20.07 | At LIS Goant 2 sets (1 as stand by) of 3 LPS each with 145 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001188 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.08 | At LIS Budriyon 2 sets (1 as stand by) of 6 LPS each with 197 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001189 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.09 | At LIS Fatehpur 2 sets (1 as stand by) of 2.41 LPS each with 21 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001190 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.1 | At LIS Killour 2 sets (1 as stand by) of 8 LPS each with 98 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001191 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.11 | At LIS Upper Bhuddi 2 sets (1 as stand by) of 8 LPS each with 55 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001192 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.12 | At LIS Khara 2 sets (1 as stand by) of 3.3 LPS each with 80 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001193 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.13 | At LIS Puruwala 2 sets (1 as stand by) of 5 LPS each with 21 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001194 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.14 | At LIS Gyayaniwala 2 sets (1 as stand by) of 4 LPS each with 25 m Total head ,at 1450 RPM, with 16 Hours Pumping | BI01010001010000000000000515BI0100001195 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | INSTRUMENTATION, CONTROL & AUTOMATION WORK-Supply, installation, testing, integration, programming & commissioning of Instrumentation, Control & Automation system for Lift Irrigation including Level Transmitter with display, Level Indicator, Level Switch, Pressure Transmitter, Gauges, Actuated Valves, Flow Meter, micro PLC based Remote Terminal Unit (RTU) along with panel mounted 10” HMI, UPS, SPD, Instrumentation Cables, Cable Trays, Earthing system etc., necessary gateways with SIM card for remote data communication and all other ancillary works and accessories required to make the system fully functional as per user requirement . Scope includes for 14 new schemes(LIS Dungi Sher, LIS Bajari 1&2, LIS Rama, LIS Jungle Bhood- Simbhalwala & Bhogpur, LIS Khairi Chandan 1&2, LIS Judag, LIS Goant, LIS Budriyon, LIS Fatehpur, LIS Killour, LIS Upper Bhuddi, LIS Khara, LIS Puruwala and LIS Gyayaniwala) Refer Data Sheet No-5 | BI01010001010000000000000515BI0100001196 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information